## Slide 1: Interlock L.Lanceri /INFN Trieste VXD Workshop, Pisa 03/10/2014
Who interlocks whom, when ?
Belle II global, (PXD + SVD) = VXD local
[“Software interlocks”  Slow Control, EPICS ]
Hardware interlock: implementation ?

## Slide 2: 1. Who interlocks whom, when?
?
?
?

## Slide 3: Who ?
Tentative list of (hardware) interlock sources for VXD
  VXD/Belle II beam abort
  SuperKEKB beam abort (injection?)
  VXD Temperature: NTC thermistors
  VXD Humidity: sniffers + Vaisala sensors
  VXD CO2 cooling plant
  Earthquake sensors ?
  Fire detectors in the experimental hall ?
  … more? Alarms/signals from nearby subdetectors, SuperKEKB, …?
Software interlocks: EPICS
  Full conditions information available, programming flexibility
  Not considered here, it is a separate issue
A complete list of interlock sources is needed

## Slide 4: Example: NTCs ELMB readout & interlock
detector
docks
up to
6 x 16 = 96
NTC sensors
Box in Electronics Hut
PC
CANbus
ELMB
ELMB
ELMB
Power supply
≈ 3÷4 m
16 twisted
pairs
(no shield)
shielded
Twisted
pairs (16)
(shield
grounded
at docks)
current
sources
HW Interlock
to main
interlock
EPICS
Slow Control

## Slide 5: Whom ?
Tentative list of (hardware) interlock recipients in VXD
  PXD power supplies: global or by subsections ?
  SVD power supplies: global or by subsections ?
  … more?
Other recipients of VXD-generated interlocks
  Global Belle II interlock system ?
  Neighbor subdetectors ?
  … others?
A complete list of interlock recipients is needed

## Slide 6: When ?
In principle, simple logical OR of different sources
  VXD/Belle II beam abort
  SuperKEKB beam abort (+ injection?)
  VXD Temperature: NTC thermistors, if temperature above threshold
  VXD Humidity: sniffers + Vaisala sensors, if Dew Point > -30oC
  VXD CO2 cooling plant, shut down or failure, CO2 leaks etc.
  … etc
To be implemented in “permit” mode
  defective connections or missing conditions generate an interlock
More refined interlock conditions and outputs ?
  Ramp down only parts of the PXD or SVD ?
  Flexibility/programmability, implementation issues, see below

## Slide 7: 2. Belle II global interlocks and VXD…
Nakayama-san is coordinating the overall Belle II Monitoring and Interlocks
see 16th B2GM report (mainly monitoring discussed up to now)

## Slide 8: 3. VXD Hardware interlock: implementation ?
?
?

## Slide 9: VXD Interlock Implementation ?
Requirements, in order of priority:
  Reliability, availability of spares, uniformity across Belle II/SuperKEKB
  Independence from network & software
  Some flexibility/programmability
    partial interlocks ?
    evolving interlock conditions and requirements ?
Possible implementations, in order of complexity:
  Hardwired OR of inputs (standardized across Belle II ?)
    Examples: SIAM modules in BaBar, Beam Abort units in SuperKEKB
  More complex decision logics (i.e. FPGA-based), custom made or commercial (standardized across Belle II ??)
  Industry-standard, commercial Programmable Logic Controllers (PLC)
    For instance Siemens PLCs, adopted by some experiments

## Slide 10: “Low end” implementation examples
BaBar/PEP-II “SIAM” modules
SuperKEKB abort modules
In both cases, essentially
hardwired ORs of inputs

## Slide 11: “high end” implementation example
Siemens PLC (Programmable Logic Controller)
in a subdetector at LHC
PLCs (or similar approaches) an overkill?
It depends on the global Belle II decisions

## Slide 12: Conclusions, To Do
Who? a complete list of interlock sources is needed
  VXD Temperature, humidity, leaks, …; Belle II, SuperKEKB
Whom? a complete list of interlock recipients is needed
  PXD, SVD power supplies, (granularity), …; Belle II, SuperKEKB
When? interlocking conditions need to be defined
  (thresholds, combined conditions, etc.)
Implementation
  Reliability; some flexibility (masks etc.); uniformity across Belle II !