## Slide 1: Mechanics & IBBelle
No news on PXD Mechanics in general
Cooling blocks for thermal mock up are at DESY
2 more blocks delivered (no surface treatment, for pressure tests)
8 more blocks in work (with surface treatment)
Some issues with electrical resistance between blocks (see next slides)

## Slide 2: Cooling Blocks
For proper grounding: R < 0.5 W between blocks
(translates into < 1 W for half shelf)
1st shelf: 0.6 W
2nd shelf: 1W
Some variations (aging?) observed
(2.9W => 3.6W in 9 months for one tube)
Electrical connection between blocks:
4 carbon tubes (also for air cooling)
Al coated
Connected to block via silver loaded
Epoxy and silver loaded paint

## Slide 3: Thermal Cycling
Thermal cycling -40°C - +50°C
No dramatic changes, but slight increase of resistivity, seems to saturate…

## Slide 4: Irradiations
Neutron irradiations: 2x10^12n/cm²: no or only slight changes (but some tracks broken)
Gamma Irradiations: 130kRad (Co60): slight increase of resistance (200W -> 250W)

## Slide 5: Test setups
Spring loaded contact has best conductivity and does not rely on conductive paint
Need to modify cooling blocks to integrate spring tube (to be studied)
Bare tube: ~0.8 W
~7.1 W
~4.5 W
~40 MW/220 kW -> 3-10 W
~1.3 W

## Slide 6: IBBelle
Original plan: copy IBL unit, assembly in a 40’ container
However: no space in Tsukuba hall, extra building too expensive
=> Use only one unit to fit in 20’ container and in Tsukuba hall
Sven .Vogt
Tel.:+49 8932354336
E-Mail:vog@mpp.mpg.de

## Slide 7: IBBelle for VXD option: add 2nd unit later
CO2 base frame für 1 Einheit

## Slide 8: Akku Unit
Heat exchanger re-designed
Akku ordered
Frame in work

## Slide 9: Chiller Unit
Chiller ordered
Frame in work

## Slide 10: CO2 Unit
Pumps delivered (2 sets)
Frame is ready
Assembly about to start

## Slide 11: Control Cabinet
Cabinet ready
Next: cabling

## Slide 12: IBBelle base frame
Adjustable feet
Can be put on wheels (bogies)

## Slide 13: IBBelle base frame
Frame assemble
Wooden panels ordered
Next: put Cabinet and frames in poition

## Slide 14: Weight: ~ 4t
ca. 600kg
ca.400kg
ca.800kg
ca. 500kg
ca. 1000kg
Crane at KEK: max load 4.5t + 25% (include support lever!)

## Slide 15: Other components
Manifold Boxes
In work

## Slide 16
Junction box
In work

## Slide 17: Components for flex tubes
Dismountable & rotatable concentric joint (at manifold)
- In work

## Slide 18: Components for flex tubes
Split (in-flow and return) at Belle side
- In work

## Slide 19: Flex Lines
Need to decide where to produce
CERN willing to help
But need manpower
To be discussed
Material can be ordered once exact length is known

## Slide 20: Location at KEK
Old PS, will be removed
Ok for IBBelle
New PS
Can these pillars/tubes be removed for 2nd unit?

## Slide 21
Thanks